## Fr
Caractéristique | Spécifications distributeur pour biométhane injecté | Spécifications transporteur pour biométhane injecté | Commentaires | Solution innovante proposée | CAPEX prévisionnel | OPEX prévisionnel | Environnement extérieur nécessaire (si solution technologique) | Description de la solution
Pouvoir Calorifique Supérieur (conditions de combustion 0 °C et 1,01325 bar) | Gaz de type H : 10,7 à 12,8 kWh/m3(n) (combustion 25°C : 10,67 à 12,77) | Gaz de type H(1) : 10,7 à 12,8 kWh/m3(n) (combustion 25°C : 10,67 à 12,77) | Calculé à partir des concentrations en hydrocarbures (C1 à C3), N2, CO2 ou mesuré à partir d'une corrélation. Ref : NF EN ISO 6976 et NF EN ISO 6974 Nécessite l'obtention d'un certificat d'examen de type auprès du LNE pour l'aspect facturation (peut être obtenu a posteriori) | Ex : analyseur par corrélation
| Gaz de type B : 9,5 à 10,5 kWh/m3(n) (combustion 25°C : 9,48 à 10,47) | Gaz de type B(1) : 9,5 à 10,5 kWh/m3(n) (combustion 25°C : 9,48 à 10,47)
Indice de Wobbe (conditions de combustion 0 °C et 1,01325 bar) | Gaz de type H : 13,64 à 15,70 kWh/m3(n) (combustion 25°C:13,6 à 15,66) | Gaz de type H : 13,64 à 15,70 kWh/m3(n) (combustion 25°C:13,6 à 15,66) | Calculé à partir des concentrations en hydrocarbures (C1 à C3), N2, CO2 ou mesuré à partir d'une corrélation. Ref : NF EN ISO 6976 et NF EN ISO 6974
| Gaz de type B : 12.01 à 13,06 kWh/m3(n) (combustion 25°C : 11,97 à 13,03) | Gaz de type B : 12.01 à 13,06 kWh/m3(n) (combustion 25°C : 11,97 à 13,03)
Densité | Comprise entre 0,555 et 0,70 | Comprise entre 0,555 et 0,70 | Calculé à partir des concentrations en hydrocarbures (C1 à C3), N2, CO2 ou mesuré à partir d'une corrélation. Ref : NF EN ISO 6976 et NF EN ISO 6974
Point de rosée eau | Inférieur à -5°C à la Pression Maximale de Service du réseau en aval du Raccordement | Inférieur à -5°C à la Pression Maximale de Service du réseau en aval du Raccordement
Point de rosée hydrocarbures | Inférieur à -2°C de 1 à 70 bar | Inférieur à -2°C de 1 à 70 bar |  | Ex : capteur spécifique
Teneur en soufre total | Inférieure à 30 mgS/m3(n) | Inférieure à 30 mgS/m3(n) | Méthode de référence : NF EN ISO 19739 | Ex : modélisation de la teneur en fonction de la caractérisation de l'épuration
Teneur en soufre mercaptique | Inférieure à 6 mgS/m³(n) | Inférieure à 6 mgS/m³(n) | Méthode de référence : NF EN ISO 19739
Teneur en soufre de H2S + COS | Inférieure à 5 mgS/m³(n) | Inférieure à 5 mgS/m³(n) | Méthode de référence : NF EN ISO 19739
Teneur en CO2 | Inférieure à 2,5 % / dérogation : gaz H : 3,5% / gaz B : 11,7% | Inférieure à 2,5 % | Méthode de référence : NF EN ISO 6974
Teneur en Tétrahydrothiophène | Comprise entre 15 et 40 mg/m³(n) | Comprise entre 15 et 40 mg/m³(n) | Méthode de référence : NF EN ISO 19739
Teneur en O2 | Inférieure à 100 ppm / dérogation gaz H : 0,7% / gaz B : 3% | Inférieure à 100 ppm
Hg | Inférieur à 1 µg/m³(n) | Inférieur à 1 µg/m³(n) | Méthode de référence : NF EN ISO 6978
Cl | Inférieur à 1 mg/m³(n) | Inférieur à 1 mg/m³(n)
F | Inférieur à 10 mg/m³(n) | Inférieur à 10 mg/m³(n)
H2 | Inférieur à 6 % | Inférieur à 6 %
NH3 | Inférieur à 3 mg/m³(n) | Inférieur à 3 mg/m³(n)
CO | Inférieur à 2 % | Inférieur à 2 %
Teneur en poussières | Inférieure à 5 mg/m3(n) | RAS

## EN
Characteristic | Specifications for biomethane injected into the Distribution network | Specifications for biomethane injected into the Transport network | Comments | Proposed Innovative Solution | Projected CAPEX | Projected OPEX | Required external environment (if technological solution) | Description of the solution
Higher Heating Value (combustion conditions: 0 °C and 1,01325 bar) | H type gas : 10,7 à 12,8 kWh/m3(n) (combustion 25°C : 10,67 to 12,77) | H type gas (1) : 10,7 à 12,8 kWh/m3(n) (combustion 25°C : 10,67 to 12,77) | Calculated from hydrocarbons (C1 to C3), N2, CO2 contents or measured from a correlation. Ref : NF EN ISO 6976 and NF EN ISO 6974 This requires the obtention of a type examination certificate delivered by LNE for billing purposes (can be obtained a posteriori) | Ex : Correlation Analyzer
| L type gas : 9,5 to 10,5 kWh/m3(n) (combustion 25°C : 9,48 to 10,47) | L type gas : 9,5 to 10,5 kWh/m3(n) (combustion 25°C : 9,48 to 10,47)
Wobbe Index (combustion conditions: 0 °C and 1,01325 bar) | H type gas : 13,64 to 15,70 kWh/m3(n) (combustion 25°C:13,6 to 15,66) | H type gas : 13,64 to 15,70 kWh/m3(n) (combustion 25°C:13,6 to 15,66) | Calculated from hydrocarbons (C1 to C3), N2, CO2 contents or measured from a correlation. Ref : NF EN ISO 6976 and NF EN ISO 6974
| L type gas : 12,01 to 13,06 kWh/m3(n) (combustion 25°C : 11,97 to 13,03) | L type gas : 12,01 to 13,06 kWh/m3(n) (combustion 25°C : 11,97 to 13,03)
Density | Between 0,555 and 0,70 | Between 0,555 and 0,70 | Calculated from hydrocarbons (C1 to C3), N2, CO2 contents or measured from a correlation. Ref : NF EN ISO 6976 and NF EN ISO 6974
Water dew point | Below -5°C at Maximum Service Pressure on the system below the Connection | Below -5°C at Maximum Service Pressure on the system below the Connection
Hydrocarbon dew point | Below -2°C from 1 to 70 bar | Below -2°C from 1 to 70 bar |  | Ex : Specific sensor
Total Sulphur content | Less than 30 mgS/m3(n) | Less than 30 mgS/m3(n) | Reference method : NF EN ISO 19739 | Ex : Modelling of the content depending on the characterization of the purification
Total mercaptan Sulphur content | Less than 6 mgS/m³(n) | Less than 6 mgS/m³(n) | Reference method : NF EN ISO 19739
H2S + COS Sulphur content | Less than 5 mgS/m³(n) | Less than 5 mgS/m³(n) | Reference method : NF EN ISO 19739
CO2 Content | Less than 2,5 % / dispensation : H gas : 3,5% / L gas : 11,7% | Less than 2,5 % | Reference method : NF EN ISO 6974
Tetrahydrothiophene content | Between 15 and 40 mg/m³(n) | Between 15 and 40 mg/m³(n) | Reference method : NF EN ISO 19739
O2 Content | Less than 100 ppm / dispensation for gaz H : 0,7% / gaz B : 3% | Less than 100 ppm
Hg | Less than 1 µg/m³(n) | Less than 1 µg/m³(n) | Reference method : NF EN ISO 6978
Cl | Less than 1 mg/m³(n) | Less than 1 mg/m³(n)
F | Less than 10 mg/m³(n) | Less than 10 mg/m³(n)
H2 | Less than 6 % | Less than 6 %
NH3 | Less than 3 mg/m³(n) | Less than 3 mg/m³(n)
CO | Less than 2 % | Less than 2 %
Dust content | Less than 5 mg/m3(n) | NTR